Din rail mounted energy meter modbus address

This manual is applicable to the product model

-DTS1946-4P

-DTSF1946-4P

Content

1. Modbus-RTU communication	3

1.1 message format 	3

1.2 Communication address information table	3

2. DL/T 645 communicating protocol	10

2.1transfer characteristic	10

2.2Application description	11

2.3 DL/T 645-1997 communicating protocol	14

2.3.1 Electric energy data	14

2.3.2 Variable data	14

2.3.3 Parametric data	15

2.4 DL/T 645-2007 communicating protocol	15

2.4.1 Electric energy data	15

2.4.2 Variable data	16

2.4.3 Total harmonic distortion data	18

2.4.4 Demand data	19

2.4.5 Reference data	19

1. Modbus-RTU communication

1.1 Message format

Read data register value (function code 0x03/0x04)

| master request | frame structure | address code | FC | numeric data code | check code |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Start register address | Number of registers |  |
|  | occupied byte | 1byte | 1byte | 2byte | 2byte | 2byte |
|  | data area | 1～247 | 0x03/0x04 |  | Max 100 | CRC16 |
|  | examples of messages | 0x01 | 0x03 | 0x00 0x00 | 0x00 0x06 | 0xC5 0xC8 |
| Slave response | frame structure | address code | FC | numeric data code | check code |
|  |  |  |  | Register bytes | register value |  |
|  | occupied byte | 1byte | 1byte | 2byte | 12byte | 2byte |
|  | examples of messages | 0x01 | 0x03 | 0x0C | 12 | CRC16 |

Note: The start register address of the host request is the data header address of the query. The number of the registers is the length of the query data. For example, the address of the upper start register is the "0x0000", and the number of the registers is 6 (0x0006).

Write setting register (function code 0x10)

| master request | frame structure | address code | FC | numeric data code | check code |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Start register address | Number of registers |  |
|  | occupied byte | 1byte | 1byte | 2byte | 2byte | 2byte |
|  | data area | 1～247 | 0x10 | 0x0802 | Max 100 | CRC16 |
|  | examples of messages | 0x01 | 0x10 | 0x08 0x02 | 0x00 0x06 | 0x2FE2 |
| Slave response | frame structure | address code | FC | numeric data code | check code |
|  |  |  |  | Register bytes | register value |  |
|  | occupied byte | 1byte | 1byte | 2byte | 12byte | 2byte |
|  | examples of messages | 0x01 | 0x10 | 0x08 0x02 | 0x00 0x01 | 0xA269 |

Note: Please set the information address table in strict accordance with the following instrument when writing the setting register. Do not attempt to modify the unused area. The write data does not allow the setting range to be exceeded. The wrong write-setting register has the potential to cause the instrument to work abnormally. Be careful.

1.2 MODBUS-RTU Address Information

Data register:

| Address | Format | Data description | Unit | R/W |
| --- | --- | --- | --- | --- |
| 0000-0001 | float | A phase voltage | V | R |
| 0002-0003 | float | B phase voltage | V | R |
| 0004-0005 | float | C phase voltage | V | R |
| 0006-0007 | float | AB line voltage | V | R |
| 0008-0009 | float | BC line voltage | V | R |
| 000A-000B | float | CA line voltage | V | R |
| 000C-000D | float | A phase current | A | R |
| 000E-000F | float | B phase current | A | R |
| 0010-0011 | float | C phase current | A | R |
| 0012-0013 | float | A Phase active power | kW | R |
| 0014-0015 | float | B Phase active power | kW | R |
| 0016-0017 | float | C Phase active power | kW | R |
| 0018-0019 | float | Total active power | kW | R |
| 001A-001B | float | A Active power | kvar | R |
| 001C-001D | float | B Active power | kvar | R |
| 001E-001F | float | C Active power | kvar | R |
| 0020-0021 | float | Total reactive power | kvar | R |
| 0022-0023 | float | A Phase view power | kVA | R |
| 0024-0025 | float | B Phase view power | kVA | R |
| 0026-0027 | float | C Phase view power | kVA | R |
| 0028-0029 | float | Total apparent power | kVA | R |
| 002A-002B | float | A Phase power factor | - | R |
| 002C-002D | float | B Phase power factor | - | R |
| 002E-002F | float | C Phase power factor | - | R |
| 0030-0031 | float | Total power factor | - | R |
| 0032-0033 | float | frequency | Hz | R |
| 0034-0035 | float | Positive Active Power | kWh | R |
| 0036-0037 | float | Reverse Active Power | kWh | R |
| 0038-0039 | float | Positive reactive power | kvarh | R |
| 003A-003B | float | Reverse reactive power | kvarh | R |
| 003C-00FF | -- | -- | -- | -- |
| 0100 | Int | Time (high byte: year, low byte: month) | - | R |
| 0101 | Int | Time (high byte: day, low byte: time) | - | R |
| 0102 | Int | Time (high byte: minute, low byte: second) | - | R |
| 0103-0105 | -- | -- | -- | -- |
| 0106-0107 | Long | Positive Active Power | 10Wh | R |
| 0108-0109 | Long | Reverse Active Power | 10Wh | R |
| 010A-010B | Long | Positive reactive power | 10varh | R |
| 010C-010D | Long | Reverse reactive power | 10varh | R |
| 010E-010F | Long | Sight electrical energy | 10VAh | R |
| 0110-0111 | Long | First quadrant reactive power | 10varh | R |
| 0112-0113 | Long | Second quadrant reactive power | 10varh | R |
| 0114-0115 | Long | Third quadrant reactive power | 10varh | R |
| 0116-0117 | Long | Fourth quadrant reactive power | 10varh | R |
| 0118-0119 | Long | Active Power [Total] | 10Wh | R |
| 011A-011B | Long | Active power [tip] | 10Wh | R |
| 011C-011D | Long | Active power [peak] | 10Wh | R |
| 011E-011F | Long | Active Power [Flat] | 10Wh | R |
| 0120-0121 | Long | Active Power [Valley] | 10Wh | R |
| 0122-0123 | Long | Active Power this month [Total] | 10Wh | R |
| 0124-0125 | Long | Active Power this month[tip] | 10Wh | R |
| 0126-0127 | Long | Active Power this month[Peak] | 10Wh | R |
| 0128-0129 | Long | Active Power this month[Flat] | 10Wh | R |
| 012A-012B | Long | Active Power this month[Valley] | 10Wh | R |
| 012C-012D | Long | Active Power Last month[total] | 10Wh | R |
| 012E-012F | Long | Active Power last month[tip] | 10Wh | R |
| 0130-0131 | Long | Active Power last month[Peak] | 10Wh | R |
| 0132-0133 | Long | Active Power last month[Flat] | 10Wh | R |
| 0134-0135 | Long | Active Power last month[Valley] | 10Wh | R |
| 0136-0137 | Long | Active power the month before last month | 10Wh | R |
| 0138-0139 | Long | Active power the month before last month[T] | 10Wh | R |
| 013A-013B | Long | Active power the month before last month[P] | 10Wh | R |
| 013C-013D | Long | Active power the month before last month[F] | 10Wh | R |
| 013E-013F | Long | Active power the month before last month[V] | 10Wh | R |
| 0140-01FF | -- | -- | -- | -- |
| 0200 | Int | A phase voltage | 0.1V | R |
| 0201 | Int | B phase voltage | 0.1V | R |
| 0202 | Int | C phase voltage | 0.1V | R |
| 0203 | Int | AB line voltage | 0.1V | R |
| 0204 | Int | BC line voltage | 0.1V | R |
| 0205 | Int | CA line voltage | 0.1V | R |
| 0206 | Int | A phase current | 0.01A | R |
| 0207 | Int | B phase current | 0.01A | R |
| 0208 | Int | C phase current | 0.01A | R |
| 0209 | Int | A Phase active power | 10W | R |
| 020A | Int | B Phase active power | 10W | R |
| 020B | Int | C Phase active power | 10W | R |
| 020C | Int | Total active power | 10W | R |
| 020D | Int | A Active power | 10var | R |
| 020E | Int | B Active power | 10var | R |
| 020F | Int | C Active power | 10var | R |
| 0210 | Int | Total reactive power | 10var | R |
| 0211 | Int | A Phase view power | 10VA | R |
| 0212 | Int | B Phase view power | 10VA | R |
| 0213 | Int | C Phase view power | 10VA | R |
| 0214 | Int | Total apparent power | 10VA | R |
| 0215 | Int | A Phase power factor |  | R |
| 0216 | Int | B Phase power factor |  | R |
| 0217 | Int | C Phase power factor |  | R |
| 0218 | Int | Total power factor |  | R |
| 0219 | Int | frequency | 0.01Hz | R |
| 021A-05FF | -- | -- | -- | -- |
| 0600 | Int | Maximum phase voltage | 0.1V | R |
| 0601 | Int | Maximum line voltage | 0.1V | R |
| 0602 | Int | Maximum current | 0.01A | R |
| 0603 | Int | Maximum active power | 10W | R |
| 0604 | Int | Maximum reactive power | 10var | R |
| 0605 | Int | Maximum apparent power | 10VA | R |
| 0606 | Int | Maximum active power requirement | 10W | R |
| 0607 | Int | Maximum reactive power requirement | 10var | R |
| 0608 | Int | Maximum apparent power requirement | 10VA | R |
| 0609 | Int | Maximum phase voltage this month | 0.1V | R |
| 060A | Int | Maximum line voltage this month | 0.1V | R |
| 060B | Int | Maximum current this month | 0.01A | R |
| 060C | Int | Maximum active power this month | 10W | R |
| 060D | Int | Maximum reactive power this month | 10var | R |
| 060E | Int | Maximum power available this month | 10VA | R |
| 060F | Int | Maximum active power requirement this month | 10W | R |
| 0610 | Int | Maximum reactive power requirement this month | 10var | R |
| 0611 | Int | Maximum power requirement this month | 10VA | R |
| 0612 | Int | Current active power requirements | 10W | R |
| 0613 | Int | Current reactive power requirements | 10var | R |
| 0614 | Int | Current apparent power requirement | 10VA | R |
| 0615 | Int | Average phase voltage | 0.1V | R |
| 0616 | Int | Average line voltage | 0.1V | R |
| 0617 | Int | Current average | 0.01A | R |
| 0618 | Int | Average active power | 10W | R |
| 0619 | Int | Average reactive power | 10var | R |
| 061A | Int | Average apparent power | 10VA | R |
| 0061B | -- | -- | -- | -- |
| 061C | char | Time recorded on power (high byte: times, low byte: years) |  | R |
| 061D | char | Time recorded on power (high byte: month, low byte: day) |  | R |
| 061E | char | Time recorded on power (high byte: time, low byte: fraction) |  | R |
| 061F | char | Timing of programming records (high byte: number of times, low byte: year) |  | R |
| 0620 | char | Time recorded by programming (high byte: month, low byte: day) |  | R |
| 0621 | char | Timing of programming records (high byte: time, low byte: fraction) |  | R |
| 0622 | char | Time of power clearing (high byte: times, low byte: years) |  | R |
| 0623 | char | Time of power clearing (high byte: month, low byte: day) |  | R |
| 0624 | char | Time for zeroing (high byte: time, low byte: minute) |  | R |

Set register:

| Address | form | Data description | Unit | R/W |
| --- | --- | --- | --- | --- |
| 0801 | Int | High byte: Power pulse constant | 0x00: 400imp/kWh 0x01: 800imp/kWh 0x02:1600imp/kWh | R/W |
| 0802 | Int | High byte: loop display | 0x01: Cycle display !(0x01):Invalid cycle | R/W |
|  |  | Low byte: Power up display interface | 0x00:U, 0x01:I 0x02:F, 0x03:P 0x04:Q, 0x05:S 0x06:PF, 0x07:E | R/W |
| 0803 | -- | -- | -- | -- |
| 0804 | Int | High byte: Instrument address | 1-247 | R/W |
|  |  | Low byte: baud rate | 0: 300bps 1: 600bps 2：1200bps 3：2400bps 4：4800bps 5：9600bps |  |
| 0805 | Int | High byte: communication data format | 0：N,8,1 1：E,8,1 2：O,8,1 3：N,8,2 | R/W |
| 0806-0810 | -- | -- | -- | -- |
| 0811 | Int | Current change ratio |  | R/W |
| 0812-081F | -- | -- | -- | -- |
| 0820 | Int | Required items | Default active reactive power apparent power | R |
| 0821 | Int | Work mode required | 0： Sliding block 1： stationary block | R/W |
| 0822 | Int | Demand slip time（t） | 1～9999s | R/W |
| 0823 | Int | Demand cycle（T） | 1～30t | R/W |
| 0824-0843 | -- | -- | -- | -- |
| 0844 | Int | First set of day rates #1 period start time | Fixed 00h：00min | R/W |
| 8045 | Int | First set of day rates #2 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 8046 | Int | First set of day rates #3 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 8047 | Int | First set of day rates #4 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 8048 | Int | First set of day rates #5 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 8049 | Int | First set of day rates #6 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 804A | Int | First set of day rates #7 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 804B | Int | First set of day rates #8 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 804C | Int | First set of day rates #9 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 804D | Int | First set of day rates #10 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 804E | Int | First set of day rates #11 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 084F | Int | First set of day rates #12 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0850 | Int | Second set of day rates #1 period start time | 固定为00h：00min | R/W |
| 0851 | Int | Second set of day rates #2 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0852 | Int | Second set of daily rate tables #3 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0853 | Int | Second set of day rates #4 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0854 | Int | Second set of day rates #5 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0855 | Int | Second set of day rates #6 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0856 | Int | Second set of day rates #7 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0857 | Int | Second set of day rates #8 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0858 | Int | Second set of day rates #9 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 0859 | Int | Second set of day rates #10 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 085A | Int | Second set of day rates #11 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 085B | Int | Second set of day rates #12 period start time | High byte :00-23:00h Low byte :00-59 minutes | R/W |
| 085C | Int | Schedule #1 and #2 rates for the first set of day rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 085D | Int | Schedule #3 #4 of the first set of day rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 085E | Int | Schedule #5,#6 of the first set of day rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 085F | Int | Schedule #7 and #8 rates for the first set of day rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0860 | Int | First set of days rate table #9,#10 | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0861 | Int | First set of day rates #11#12 | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0862 | Int | Schedule #1 and #2 rates for the second set of daily rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0863 | Int | Schedule #3#4 of the second set of daily rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0864 | Int | Schedule #5#6 of the second set of daily rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0865 | Int | Schedule #7 and #8 rates for the second set of day rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0866 | Int | Second set of daily rate statement #9,#10 period rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0867 | Int | Second set of daily rate table #11,#12 period rates | High Byte :#1 Time Rate Low byte :#2 time period rate 0-tip ,1-peak, 2-Flat ,3-valley | R/W |
| 0868 | Int | Monthly rates (January/February) | High byte: January-day rate table Low byte: February-day rate table 0： First set of daily rates 1： second set of daily rates | R/W |
| 0869 | Int | Monthly rates (March/April) | High byte: March day rate table Low byte: April-day rate table 0： First set of daily rates 1： second set of daily rates | R/W |
| 086A | Int | Monthly rates (May/June) | High byte: May Day rate table Low byte: June-day rate table 0： First set of daily rates 1： second set of daily rates | R/W |
| 086B | Int | Monthly rate schedule (July/August) | High byte: July Day rate table Low byte: daily August rate table 0： First set of daily rates 1： second set of daily rates | R/W |
| 086C | Int | Monthly rates (9 October) | High byte: September-day rate table Low byte: October-day rate table 0： First set of daily rates 1： second set of daily rates | R/W |
| 086D | Int | Monthly rates (11 December) | High byte: November Day rate table Low byte: December day rate table 0： First set of daily rates 1： second set of daily rates | R/W |
| 086E | Int | Meter reading day | High byte :00-23:00h Low byte :00-59 minutes | R/W |

2. DL/T 645 Communicating protocol

2.1 Transfer characteristic

The main-slave half-duplex communication mode and the establishment and cancellation of communication links are controlled by the information frames sent by the main station. Each frame has a frame starter, which is composed of seven parts: station address domain, control code, data length, frame information longitudinal check code and frame Terminator. Each part consists of a number of bytes.

Half dual port communication mode, baud rate: 1200bps;

Byte format: each byte contains 8-bit binary code, with a starting bit (0), an even check bit and a stop bit (1). The transmission sequence as shown in figure 1.D0 is the lowest valid bit of bytes and D 7 is the highest valid bit of bytes. Pass low first, then pass high.

| 0 | D0 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | P | 1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Transmission direction

start bit                 8 bit data          Parity check bit  stop bit

Figure 1 byte transmission sequence

| explain | code |
| --- | --- |
| frame start | 68H |
| address field | A0 A1 A2 A3 A4 A5 |
| frame start | 68 |
| control code | C |
| Data length domain | L |
| data field | DATA |
| check code | CS |
| tailed | 16H |

The frame format is shown below.

Address field A0-A5:2-bit BCD code per byte. The low address is before and the high address is after. When the address is 99 99 99 99 99 H, it is the broadcast address.

The communication address uses the table number, and at least 2 bits or more of the low table number bit can be entered to communicate. Less input can be easily operated.

Control code C: the format of the control code.

D7＝0：The command frame sent by the master station.

D7＝1：A response frame sent from the station.

D6＝0：Answer correctly from the station.

D6＝1：slave response to abnormal information.

D5＝0：No post-read data frame.

D4～D0：Request and answer function code.

00001：read data

00100：Write data

01000：broadcast school

01111：Modify the password

Data length L: the number of bytes in the data field, hexadecimal number.

The data field data: the data field includes data identification and data whose structure changes with the function of the control code. At the time of transmission, the sender adds the 33H process according to the byte, and the receiver performs the 33H process according to the byte.

The sum of the modulo 256 of all the bytes prior to the start of the frame start to the check code, i. e., the binary arithmetic sum of the bytes, and the overflow value of not more than 256.

The end of the frame information is indicated by the end of the frame information 16h.

Preamble byte:Before sending frame information, send 1-4 FEHs to wake up the receiver.

Transmission order: All data items should be first transferred to lower byte and then high byte.

Transmission response:each communication is started by the master station sending a request command frame to the slave station selected according to the address field of the information frame, and the requested slave station responds according to the requirements of the control code in the command frame.

The response delay Td:20ms ≤ Td ≤ 500ms after receiving the command frame,

Pause time between bytes Tb: Tb ≤ 500ms

Error control: the byte check is even, the frame check is longitudinal information checksum, the receiver abandons the information frame regardless of the parity error or longitudinal information checksum error, and does not respond.

2.2 Application description

Read data:

Master station request frame

function request read data

Control code C =01H.

Data length L = 02H

Frame format:

Function from station to normal response

Control code C = 81H

Data length L ≤ 02H m (data length)

data frame format

Slave station anomaly response frame

The function receives an illegal data request or no such data from the station

Control code C = C1H

Frame format:

Write data:

Write data request frame

The functional master station requests setting data (or programming) from the slave station

Control code C = 04H

Data length L ≤ 02H m (data length) password 4 bytes

Frame format:

| 68H | A0 | .. | A5 | 68H | 04H | L | DI0 | DI1 | PAn | P0N | P1N | P2N | N1 | 。。 | Nm | CS | 16H |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

From the station normal response frame.

the function informs the master station of the result of the execution of the request command

Control code C = 84H

Data length L = 00H

| 68H | A0 | 。。。 | A5 | 68H | 84H | 00H | CS | 16H |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Frame format:

slave station anomaly response frame

Control code C=C4H

Data length L = 01H

Frame format:

| 68H | A0 | 。。。 | A5 | 68H | C4H | 01H | ERR | CS | 16H |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

broadcast school

Functions Synchronize slave and master station time.

Control code C = 08H

Data length L = 06H

Data field YYMMDDhhhmss

Frame format:

| 68H | 99H | … | 99H | 68H | 08H | 06H | ss | mm | hh | DD | MM | YY | CS | 16H |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Note:

1. No response is required when broadcasting school.

2. Broadcasting schools are not allowed to be implemented within the range of 23 / 50 / 10.

3.School hours can only be allowed once a day, with a range of 30 seconds per minute. The maximum allowable error in broadcasting school is ±20 minutes.

To modify the password:

Write password request frame

The function changes the current password from the station

Control code C = 0 FH

Data length L = 08H

Data domain PA 0 P 00 P 10 P 20 PAN P 0 NP 1 NP 2 N.

Frame format:

| 68H | A0 | … | A5 | 68H | 0FH | 08H | PA0 | P00 | P10 | P20 | PAN | P0N | P1N | P2N | CS | 16H |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

P00P10P20 is the password of the new password or higher permission. PA0 represents the password permission: P0NP1NP2N is the new password or the password to be set, PAN is the permission of the new password. PA0, the value range of PAN is 0 to 9, 0 is the higher the permission, the lower the numerical permission.

Radio frozen electricity

Function: freeze the power immediately after receiving the command from the station.

Control code: C = 05H

Data length: l ≤ 02H

Frame format:

| 68H | 99H | … | 99H | 68H | 05H | 02H | CS | 16H |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

2.3 DL/T 645-1997 Communication Protocol.

2.3.1 Electrical energy data

| Identification code | Data format | length | unit | Read | write | Data item name |
| --- | --- | --- | --- | --- | --- | --- |
| 9010 | XXXXXX.XX | 4 | kWh | * |  | Positive active electric energy [total] |
| 9011 | XXXXXX.XX | 4 | kWh | * |  | Forward active power [tip] |
| 9012 | XXXXXX.XX | 4 | kWh | * |  | Positive active energy[peak] |
| 9013 | XXXXXX.XX | 4 | kWh | * |  | Positive active power [flat] |
| 9014 | XXXXXX.XX | 4 | kWh | * |  | Positive active energy[valley] |
| 901F |  | 20 | kWh | * |  | Forward active power packet |
| 9020 | XXXXXX.XX | 4 | kWh | * |  | Reverse active power |
| 9110 | XXXXXX.XX | 4 | kvarh | * |  | Forward reactive power |
| 9120 | XXXXXX.XX | 4 | kvarh | * |  | reverse reactive energy |
| 9130 | XXXXXX.XX | 4 | kvarh | * |  | first-quadrant reactive power |
| 9140 | XXXXXX.XX | 4 | kvarh | * |  | fourth-quadrant reactive power |
| 9150 | XXXXXX.XX | 4 | kvarh | * |  | Second quadrant reactive power |
| 9160 | XXXXXX.XX | 4 | kvarh | * |  | third quadrant reactive power |
| 9410 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [total] last month |
| 9411 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [tip] last month |
| 9412 | XXXXXX.XX | 4 | kWh | * |  | last month active energy[peak] |
| 9413 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [flat] last month |
| 9414 | XXXXXX.XX | 4 | kWh | * |  | last month active electric energy[valley] |
| 941F |  | 20 | kWh | * |  | last month active power data packet |
| 9810 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [total] last month |
| 9811 | XXXXXX.XX | 4 | kWh | * |  | The last month was active [sharp]. |
| 9812 | XXXXXX.XX | 4 | kWh | * |  | last month active energy[peak] |
| 9813 | XXXXXX.XX | 4 | kWh | * |  | Last month active energy[Ping] |
| 9814 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [valley] last month |
| 981F |  | 20 | kWh | * |  | Active power packet last month |
| 9FFF |  | 88 | kWh | * |  | All of the above power packets |

### 2.3.2 variable data

| Identification code | data format | length | unit | read | write | Data item name |
| --- | --- | --- | --- | --- | --- | --- |
| B611 | XXXX | 2 | V | * |  | A phase voltage |
| B612 | XXXX | 2 | V | * |  | B phase voltage |
| B613 | XXXX | 2 | V | * |  | C phase voltage |
| B61F |  | 6 | V | * |  | Phase Voltage Data Pack |
| B691 | XXXX | 2 | V | * |  | AB line voltage |
| B692 | XXXX | 2 | V | * |  | BC line voltage |
| B693 | XXXX | 2 | V | * |  | CA line voltage |
| B69F |  | 6 | V | * |  | Line voltage data packet |
| B621 | XX.XX | 2 | A | * |  | A phase current |
| B622 | XX.XX | 2 | A | * |  | B phase current |
| B623 | XX.XX | 2 | A | * |  | C phase current |
| B62F |  | 6 | A | * |  | Current Data Pack |
| B630 | XX.XXXX | 3 | kW | * |  | Total active power |
| B631 | XX.XXXX | 3 | kW | * |  | A Phase active power |
| B632 | XX.XXXX | 3 | kW | * |  | B Phase active power |
| B633 | XX.XXXX | 3 | kW | * |  | C Phase active power |
| B63F |  | 12 | kW | * |  | Active power data packet |
| B640 | XX.XX | 2 | kvar | * |  | Total reactive power |
| B641 | XX.XX | 2 | kvar | * |  | A Active power |
| B642 | XX.XX | 2 | kvar | * |  | B Active power |
| B643 | XX.XX | 2 | kvar | * |  | C Active power |
| B64F |  | 8 | kvar | * |  | Reactive Power Data Pack |
| B650 | X.XXX | 2 | 0.001 | * |  | Total power factor |
| B651 | X.XXX | 2 | 0.001 | * |  | A Phase power factor |
| B652 | X.XXX | 2 | 0.001 | * |  | B Phase power factor |
| B653 | X.XXX | 2 | 0.001 | * |  | C Phase power factor |
| B65F |  | 8 | 0.001 | * |  | Power factor data packet |
| B660 | XX.XX | 2 | kVA | * |  | Total apparent power |
| B661 | XX.XX | 2 | kVA | * |  | A apparent power |
| B662 | XX.XX | 2 | kVA | * |  | B apparent power |
| B663 | XX.XX | 2 | kVA | * |  | C apparent power |
| B66F |  | 8 | kVA | * |  | Visual power packets |
| B680 | XX.XX | 2 | Hz | * |  | frequency |
| B6FF | - | 56 | - | * |  | Instantaneous Electricity Data Pack |

### 2.3.3 parametric data

| Identification code | data format | length | unit | read | write | Data item name |
| --- | --- | --- | --- | --- | --- | --- |
| C010 | YYMMDDWW | 4 | Year, month, day, week | * | * | Date and week | This identity code is invalid when there is no duplicate rate function |
| C011 | hhmmss | 3 | Time and second | * | * | time |  |
| C117 | DDhh | 2 | daytime | * | * | Automatic meter reading date |  |
| C023 | XX | 1 |  | * |  | Power meter operation status word 2 (see note) |
| C030 | NNNNNN | 3 | imp/kWh | * | * | active pulse constant |
| C031 | NNNNNN | 3 | imp/kvarh | * | * | reactive pulse constant |
| C032 | NNNNNNNNNNNN | 6 |  | * | * | Table No. (Table No. data is less than 247) |
| C331 | hhmmNN | 3 | time-division rate | * | * | Period 1 (start time default is 00:00) | The data encoding is not valid when there is no complex rate function. |
| C332 | hhmmNN | 3 | time-division rate | * | * | Period 2 |  |
| C333 | hhmmNN | 3 | time-division rate | * | * | Period 3 |  |
| C334 | hhmmNN | 3 | time-division rate | * | * | Period 4 |  |
| C335 | hhmmNN | 3 | time-division rate | * | * | Period 5 |  |
| C336 | hhmmNN | 3 | time-division rate | * | * | Time 6 |  |
| C337 | hhmmNN | 3 | time-division rate | * | * | Period 7 |  |
| C338 | hhmmNN | 3 | time-division rate | * | * | Period 8 |  |
| C339 | hhmmNN | 3 | time-division rate | * | * | Period 9 |  |
| C33A | hhmmNN | 3 | time-division rate | * | * | Period 10 |  |
| C33B | hhmmNN | 3 | time-division rate | * | * | 11th Session |  |
| C33C | hhmmNN | 3 | time-division rate | * | * | Period 12 |  |

Note:

The address of the device and the communication rate shall be changed, and the communication protocol of the multi-function electric energy meter shall be in accordance with the DL/ T645-1997 <multifunction electric energy meter communication protocol.

When you change the communication parameters,1 Byte (right) + 3 Byte (password) is required to place the identification code. The default permissions and passwords are:00000000.

3 meter running status word 2 [C023] (1: reverse, 0: forward)

| Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| total reactive direction | -- | -- | -- | Total active power direction | -- | -- | -- |

2.4 DL/T 645-2007 communicating protocol

### 2.4.1 electric energy data

| Identification code | data format | length | unit | read | write | Data item name |
| --- | --- | --- | --- | --- | --- | --- |
| 00010000 | XXXXXX.XX | 4 | kWh | * |  | Positive active electric energy [total] |
| 00010100 | XXXXXX.XX | 4 | kWh | * |  | Forward active power [tip] |
| 00010200 | XXXXXX.XX | 4 | kWh | * |  | Positive active energy[peak] |
| 00010300 | XXXXXX.XX | 4 | kWh | * |  | Positive active power [flat] |
| 00010400 | XXXXXX.XX | 4 | kWh | * |  | Positive active energy[valley] |
| 0001FF00 |  | 20 | kWh | * |  | Forward active power packet |
| 00020000 | XXXXXX.XX | 4 | kWh | * |  | Reverse active power |
| 00030000 | XXXXXX.XX | 4 | kvarh | * |  | Forward reactive power |
| 00040000 | XXXXXX.XX | 4 | kvarh | * |  | reverse reactive energy |
| 00050000 | XXXXXX.XX | 4 | kvarh | * |  | first-quadrant reactive power |
| 00060000 | XXXXXX.XX | 4 | kvarh | * |  | Second quadrant reactive power |
| 00070000 | XXXXXX.XX | 4 | kvarh | * |  | third quadrant reactive power |
| 00080000 | XXXXXX.XX | 4 | kvarh | * |  | fourth-quadrant reactive power |
| 00010001 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [total] last month |
| 00010101 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [tip] last month |
| 00010201 | XXXXXX.XX | 4 | kWh | * |  | last month active energy[peak] |
| 00010301 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [flat] last month |
| 00010401 | XXXXXX.XX | 4 | kWh | * |  | last month active electric energy[valley] |
| 0001FF01 |  | 20 | kWh | * |  | last month active power data packet |
| 00010002 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [total] last month |
| 00010102 | XXXXXX.XX | 4 | kWh | * |  | The last month was active [sharp]. |
| 00010202 | XXXXXX.XX | 4 | kWh | * |  | last month active energy[peak] |
| 00010302 | XXXXXX.XX | 4 | kWh | * |  | Last month active energy[Ping] |
| 00010402 | XXXXXX.XX | 4 | kWh | * |  | Active electricity [valley] last month |
| 0001FF02 |  | 20 | kWh | * |  | Active power packet last month |

2.4.2  Variables data

| Identification code | data format | length | unit | read | write | Data item name |
| --- | --- | --- | --- | --- | --- | --- |
| 02010100 | XXX.X | 2 | V | * |  | A phase voltage |
| 02010200 | XXX.X | 2 | V | * |  | B phase voltage |
| 02010300 | XXX.X | 2 | V | * |  | C phase voltage |
| 0201ff00 |  | 6 | V | * |  | Phase Voltage Data Pack |
| 020c0100 | XXXX | 2 | V | * |  | AB line voltage |
| 020c0200 | XXXX | 2 | V | * |  | BC line voltage |
| 020c0300 | XXXX | 2 | V | * |  | CA line voltage |
| 020cff00 |  | 6 | V | * |  | Line voltage data packet |
| 02020100 | XXX.XXX | 3 | A | * |  | A phase current |
| 02020200 | XXX.XXX | 3 | A | * |  | B phase current |
| 02020300 | XXX.XXX | 3 | A | * |  | C phase current |
| 0202ff00 |  | 9 | A | * |  | Current Data Pack |
| 02030000 | XX.XXXX | 3 | kW | * |  | Total active power |
| 02030100 | XX.XXXX | 3 | kW | * |  | A Phase active power |
| 02030200 | XX.XXXX | 3 | kW | * |  | B Phase active power |
| 02030300 | XX.XXXX | 3 | kW | * |  | C Phase active power |
| 0203ff00 |  | 12 | kW | * |  | Active power data packet |
| 02040000 | XX.XXXX | 3 | kvar | * |  | Total reactive power |
| 02040100 | XX.XXXX | 3 | kvar | * |  | A Active power |
| 02040200 | XX.XXXX | 3 | kvar | * |  | B Active power |
| 02040300 | XX.XXXX | 3 | kvar | * |  | C Active power |
| 0204ff00 |  | 12 | kvar | * |  | Reactive Power Data Pack |
| 02060000 | X.XXX | 2 | 0.001 | * |  | Total power factor |
| 02060100 | X.XXX | 2 | 0.001 | * |  | A Phase power factor |
| 02060200 | X.XXX | 2 | 0.001 | * |  | B Phase power factor |
| 02060300 | X.XXX | 2 | 0.001 | * |  | C Phase power factor |
| 0206ff00 |  | 8 | 0.001 | * |  | Power factor data packet |
| 02050000 | XX.XXXX | 3 | kVA | * |  | Total apparent power |
| 02050100 | XX.XXXX | 3 | kVA | * |  | A Phase view power |
| 02050200 | XX.XXXX | 3 | kVA | * |  | B Phase view power |
| 02050300 | XX.XXXX | 3 | kVA | * |  | C Phase view power |
| 0205ff00 |  | 12 | kVA | * |  | Visual power packets |
| 02800002 | XX.XX | 2 | Hz | * |  | frequency |

2.4.3  Total harmonic distortion data

| Identification code | data format | length | unit | read | write | Data item name |
| --- | --- | --- | --- | --- | --- | --- |
| 02080100 | XX.XX | 2 | 0.01% | * |  | A phase voltage THD |
| 02080200 | XX.XX | 2 | 0.01% | * |  | B phase voltage THD |
| 02080300 | XX.XX | 2 | 0.01% | * |  | C phase voltage THD |
| 0208ff00 |  | 6 | 0.01% | * |  | 3 phase voltage THD data packet |
| 02090100 | XX.XX | 2 | 0.01% | * |  | A phase current THD |
| 02090200 | XX.XX | 2 | 0.01% | * |  | B phase current THD |
| 02090300 | XX.XX | 2 | 0.01% | * |  | C phase current THD |
| 0209ff00 |  | 6 | 0.01% | * |  | 3 phase current THD data packet |

2.4.4 Demand data

| Identification code | data format | length | unit | read | write | Data item name |
| --- | --- | --- | --- | --- | --- | --- |
|  | XXX.X | 2 | 0.1V | * |  | Maximum phase voltage this month |
|  | XXX.X | 2 | 0.1V | * |  | Maximum line voltage this month |
|  | XXX.XXX | 3 | 1mA | * |  | Maximum current this month |
|  | XX.XXXX | 3 | 1kW | * |  | Maximum active power this month |
|  | XX.XXXX | 3 | 1kvar | * |  | Maximum reactive power this month |
|  | XX.XXXX | 3 | 1kVA | * |  | Maximum power available this month |
|  | XX.XXXX | 3 | 1kW | * |  | Maximum active demand this month |
|  | XX.XXXX | 3 | 1kvar | * |  | Maximum reactive power requirement this month |
|  | XX.XXXX | 3 | 1kVA | * |  | Maximum demand this month |
| 0101ff00 |  | 25 |  |  |  | Maximum and maximum demand packets for the month |
|  | XXX.X | 2 | 0.1V | * |  | Maximum phase voltage |
|  | XXX.X | 2 | 0.1V | * |  | Maximum line voltage |
|  | XXX.XXX | 3 | 1mA | * |  | Maximum current |
|  | XX.XXXX | 3 | 1kW | * |  | Maximum active power |
|  | XX.XXXX | 3 | 1kvar | * |  | Maximum reactive power |
|  | XX.XXXX | 3 | 1kVA | * |  | Maximum apparent power |
|  | XX.XXXX | 3 | 1kW | * |  | Maximum active demand |
|  | XX.XXXX | 3 | 1kvar | * |  | Maximum reactive power requirement |
|  | XX.XXXX | 3 | 1kVA | * |  | Maximum view demand |
| 0101ff01 |  | 25 |  |  |  | Maximum and maximum requirement packets |

### 2.4.5 parametric data

| characteristic encoded | data format | length | unit | read | write | Data item name |
| --- | --- | --- | --- | --- | --- | --- |
| 04000101 | YYMMDDWW | 4 | Year, month, day, week | * | * | Date and week | This identity code is invalid when there is no duplicate rate function |
| 04000102 | hhmmss | 3 | Time and second | * | * | time |  |
| 04000B01 | DDhh | 2 | daytime | * | * | Automatic meter reading date |  |
| 04000502 | XXXX | 2 |  | * |  | Power meter operation status word 2 (see note) |
| 04000409 | XXXXXX | 3 | imp/kWh | * |  | active pulse constant |
| 0400040a | XXXXXX | 3 | imp/kvarh | * |  | reactive pulse constant |
| 04000401 | NNNNNNNNNNNN | 6 |  | * | * | Communication address (data less than 247) |
| 04010001 (up to 36 bytes in length) | hhmmNN | 3 | time-division rate | * | * | Period 1 (start time default is 00:00) | The data encoding is not valid when there is no complex rate function. |
|  | hhmmNN | 3 | time-division rate | * | * | Period 2 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 3 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 4 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 5 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 6 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 7 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 8 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 9 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 10 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 11 |  |
|  | hhmmNN | 3 | time-division rate | * | * | Period 12 |  |

Note:

The communication address shall be written and the communication protocol of the multi-function electric energy meter shall be in accordance with the DL/ T645-2007 <multifunction electric energy meter communication protocol.

When you change the communication parameters, a 4 Byte (password) + 4 Byte (operator code) is required to place the identification code. The default password and operator code are:01010102020202.

3 meter running status word 2 [04000502] (1: reverse, 0: forward)

| Bit15 | Bit14 | Bit13 | Bit12 | Bit11 | Bit10 | Bit9 | Bit8 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| leave out | leave out | leave out | leave out | leave out | leave out | leave out | leave out |
| Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0 |
| reactive direction | leave out | leave out | leave out | active direction | leave out | leave out | leave out |